HPWHsim Technical Explanation

Update Tank Temperatures

The temperatures of the nodes in each tank are updated at the beginning of each step. The temperature profile changes due to draws and UA losses are calculated in this step.

The fractional number of nodes drawn is calculated as in Equation (1):

drawFraction = { volume of draw } wideslash { volume per Node }	(1)

The draw fraction is then divided into its whole part and its fractional part. In a typical HPWH, with a volume per node of approximately 4 gallons, most draws will be less than one node. The whole nodes are “moved upwards” in the tank by assigning the temperature of each node to the node above it and filling in the bottom node with water at the specified inlet temperature. Then the remaining partial node draw is calculated using Equation (2).

tankTemps[i] = tankTemps[i] * (1 - fraction of node) + tankTemps[ i - 1] * fraction of node	(2)

Where i is the number of the node in the node array. The bottom node, where i - 1 is negative, is mixed with water at the inlet temperature. The correctness of this calculation relies on the relative invariance of the specific heat of water with respect to temperature and the equality of node volumes.

The temperature and volume of any water shifted out of the tank is tracked and averaged to calculate the outlet temperature.

If the “mix on draw” feature is enabled for this HPWH, the bottom third of the tank experiences mixing. This is done by finding the average temperature of the bottom third. Then for each node, one third of the difference between the average and the current temperature is subtracted:

tankTemps[i] = tankTemps[i] + ((average - tankTemps[i]) / 3.0);	(3)

Next, the temperatures of the nodes are adjusted for standby losses. The average temperature of the tank is found, then the total energy lost by the tank is calculated by Equation (4):

(tankUA * (average tank temperature - ambient temperature) * (minutes per step / 60.0))	(4)

Where tankUA is measured kJ / hrC. The total losses are split equally amongst all nodes, and then the affect on temperature is calculated by Equation (5):

node temperature loss = {node energy loss} wideslash {((volume per node * density of water) * specific heat of water)}	(5)

heat source choice logic – flow chart?

heating logic – loop over heat sources; if time left, subtract used time and turn on next if !shutsOff
addHeat
calcHeatDist
getCapacity
addHeatAboveNode – heat percent according to heatDist
OR addHeatExternal